“REQUEST FOR AUTHORISATION” FORMS

FORM C1

| LINE NO | ‘REQUEST FOR AUTHORISATION’ TO UNDERTAKE THE SETTING AND SEALING OF METER REGULATORS ON LOW PRESSURE METER INSTALLATIONS WITH BADGED METER CAPACITY NOT EXCEEDING 6M³/HR . |  |  |  |
| --- | --- | --- | --- | --- |
| 1 | Name and address of organisation submitting this request and installing the meter installation (Correspondence Address). |  | OAMI Number* (If applicable) |  |
|  |  |  | GMAM Registration Number.(Mandatory) |  |
| 2 | Name and address of OAMI requesting authorisation to break a seal, set and seal the meter regulator. |  | OAMI number (Mandatory) |  |
| 3 | Section A to be completed by the organisation requesting to install the meter installation. |  |  |  |
| 4 | I/We# warrant that any meter installation of the category defined above installed or modified by this organisation following receipt of National Grid Gas’s Letter of Authorisation will meet the following conditions: |  |  |  |
| 5 | The meter installation is designed and will be installed to comply with the requirements of BS6400-1:2002 |  |  |  |
| 6 | The meter installation is capable of sustaining a design maximum incidental pressure of 200 mbar at the inlet of the meter installation without jeopardising the integrity of any connected gas fittings, and shall have an associated Design Pressure of 75mbar. |  |  |  |
| 7 | The meter installation will ensure that for gas flow rates greater than 5% of the maximum allowable flow rate, the operating pressure at the outlet of the meter installation is maintained between 15 – 25 mbar when the pressure at the inlet of the meter installation is between DMP 19 and MOP 75 mbar. |  |  |  |
| 8 | That the meter and installation meets the requirements of Schedule 2B of the Gas Act with respect to compliance with Section 17 of the Gas Act. |  |  |  |
| 9 | That the company responsible for undertaking the installation has the appropriate GAS SAFE registration and that the individual who undertakes the work holds an appropriate and valid certificate of competence under Nationally Accredited Certification Scheme or Approved Code of Practice. |  |  |  |
| 10 | In the event that my organisation is not OAMI registered, the installation will be inspected by an OAMI in accordance with the Gas Suppliers Standard Licence Conditions. |  |  |  |
| 11 | Signed ___________________________ Organisation installing meter installation |  |  |  |
| 12 | Date ___________________________ |  |  |  |
| 13 | Position in Organisation_______________________________________ |  |  |  |

* Where applicable

 Delete as appropriate

| 14 | Section B to be completed by the organisation requesting Authorisation to break a seal, set and seal the meter regulator. |
| --- | --- |
| 15 | The regulator will be set to ensure a metering pressure of [ ] mbar7 |
| 16 | The regulator lock up pressure will not exceed [ ] mbar7 |
| 17 | Under all circumstances (including zero flow) the meter installation will protect the installation pipe work, gas fittings and any appliances from being exposed to pressures greater than [ ] 9 mbar. |
| 18 | The meter installation will be clearly labelled with its metering pressure. |
| 19 | That the company responsible for undertaking any setting or adjustment has the appropriate CORGI registration and that the individual who undertakes the work holds an appropriate and valid certificate of competence under Nationally Accredited Certification Scheme or Approved Code of Practice. |
| 20 | I confirm that this organisation is an OAMI and request Authorisation to break a seal, set and seal the meter regulator. I also confirm that a GAS SAFE registered person with appropriate competencies for this category of work will verify and ensure that the meter regulator, when installed and put to work will not exceed the values stated above. In the event that the meter regulator is adjusted the meter regulator will be subsequently sealed to prevent unauthorised adjustment with a seal marked with this organisation’s OAMI registration number. |
| 21 | Signed ________________________ Organisation requesting to break a seal, set and seal the meter regulator. |
| 22 | Date ________________________ |
| 23 | Position in Organisation _________________ e.g. Responsible Engineer/Manager |
| 24 | Section C For National Grid Gas Office use only |
| 25 | Date received: __________________________ |
| 26 | Application reference number: ________________________ |

7 Reference should be made to Appendix B for appropriate values.

9 Reference should be made to Appendix B to insert the appropriate value for regulator lockup

FORM C2

| LINE NO | REQUEST FOR AUTHORISATION TO UNDERTAKE THE SETTING AND SEALING OF METER REGULATORS ON MEDIUM PRESSURE METER INSTALLATIONS WITH BADGED METER CAPACITY NOT EXCEEDING 6M³/HR. |  |  |  |
| --- | --- | --- | --- | --- |
| 1 | Name and address of organisation submitting this request and installing the meter installation (Correspondence Address). |  | OAMI Number* (If applicable) |  |
|  |  |  | GMAM Registration Number.(Mandatory) |  |
| 2 | Name and address of OAMI requesting Authorisation to break a seal, set and seal the meter regulator and any associated pressure control and protection device(s). |  | OAMI number (Mandatory) |  |
| 3 | Section A to be completed by the organisation requesting to install the meter installation. |  |  |  |
| 4 | I/We# warrant that any meter installation of the category defined above installed or modified by this organisation following receipt of National Grid Gas’s Letter of Authorisation will meet the following conditions: |  |  |  |
| 5 | The meter installation is designed and will be installed to comply with the requirements of the IGE/TD/15. |  |  |  |
| 6 | The meter installation will be regulated and the pressure control and protection arrangements of the installation will comply with IGE/TD/15 Figure [ ]2. |  |  |  |
| 7 | The meter installation is capable of sustaining a design maximum incidental pressure at the inlet of the meter installation of 2.7 bar without jeopardising the integrity of any connected gas fittings and shall have an associated Design Pressure of 2.0 bar. |  |  |  |
| 8 | The meter installation will ensure that at gas flow rates greater than 5% of the maximum allowable flow rates, the operating pressure at the outlet of the meter installation is maintained between 15 – 25 mbar when the pressure at the inlet of the meter installation is between the DMP [ ] and MOP [ ]6. |  |  |  |
| 9 | That the meter and the installation meet the requirements of Schedule 2B of the Gas Act with respect to compliance with Section 17 of the Gas Act. |  |  |  |
| 10 | That the person undertaking the installation is GAS SAFE registered and has been assessed by our organisation as competent for this category of work. |  |  |  |
| 11 | In the event that my organisation is not OAMI registered, the installation will be inspected by an OAMI in accordance with the Gas Suppliers Standard Licence Conditions. |  |  |  |
| 12 | Signed ___________________________ Organisation installing meter installation |  |  |  |
| 13 | Date ___________________________ |  |  |  |
| 14 | Position in Organisation _______________________________________ |  |  |  |

*	Where applicable

#	Delete as appropriate

2	The applicant should state what pressure control and protection standard that is to be used and where a number of options are available to state which option is to be used.

6	The Design Minimum Pressure and the Maximum Operating Pressure as provided by National Grid Gas for the Network should be inserted at this point.

| 15 | Section B to be completed by the organisation requesting Authorisation to break a seal, set and seal the meter regulator. |
| --- | --- |
| 16 | The regulator will be set to ensure a metering pressure of [ ] mbar7 |
| 17 | The regulator lock up pressure will not exceed [ ] mbar7 |
| 18 | The relief valve will be set to open at a pressure of [ ] mbar7 |
| 19 | The final safety device will be set at a pressure of [ ] mbar7 |
| 20 | Under all circumstances (including zero flow) the meter installation will protect the installation pipe work, gas fittings and any appliances from being exposed to pressures greater than [ ] 8 mbar. |
| 21 | The meter installation will be clearly labelled with its metering pressure, the pressure any relief valve will open and the limiting pressure of any final protection device. |
| 22 | That the person undertaking any setting or adjustment is GAS SAFE registered and has been assessed by our organisation as competent for this category of work. |
| 23 | I confirm that this organisation is an OAMI and request Authorisation to break a seal, set and seal the meter regulator and any associated pressure control and protection device(s). I also confirm that a GAS SAFE registered person with appropriate competencies for this category of work will verify and ensure that the regulator and any associated pressure control and protection device(s), when installed and put to work will not exceed the values stated above. In the event that the meter regulator and any associated pressure control and protection device(s) are adjusted the meter regulator and any associated pressure control and protection device(s) will be subsequently sealed to prevent unauthorised adjustment with a seal marked with this organisation’s OAMI registration number. |
| 24 | Signed _______________________ Organisation requesting to break a seal, set and seal the meter regulator and any associated pressure control and protection device(s). |
| 25 | Date ________________________ |
| 26 | Position in Organisation ______________________ e.g. Responsible Engineer/Manager |
| 27 | Section C For National Grid Gas Office use only |
| 28 | Date received: ________________ |
| 29 | Application reference number: _________________________ |

7 Reference should be made to Appendix B for appropriate values.

8 Insert the appropriate pressure of the final protection device, normally the set pressure plus the tolerance.

FORM C3

| LINE NO | REQUEST FOR AUTHORISATION TO UNDERTAKE THE SETTING AND SEALING OF METER REGULATORS ON LOW PRESSURE, STANDARD, METER INSTALLATIONS WITH BADGED METER CAPACITY EXCEEDING 6M³/HR BUT NOT EXCEEDING 1076M³/HR (STANDARD PRESSURE SERVICE) |  |  |  |
| --- | --- | --- | --- | --- |
| 1 | Name And address of organisation submitting this request and installing the meter installation. (Correspondence Address) |  | OAMI Number* (If applicable) |  |
|  |  |  | GMAM Registration Number.(Mandatory) |  |
| 2 | Name and address of OAMI requesting Authorisation to break a seal, set and seal the meter regulator. |  | OAMI Number (Mandatory) |  |
| 3 | Section A to be completed by the organisation requesting to install the meter installation. |  |  |  |
| 4 | I/We# warrant that any meter installation of the category defined above installed or modified by this organisation following receipt of National Grid Gas’s Letter of Authorisation will meet the following conditions: |  |  |  |
| 5 | The meter installation is designed and will be installed to comply with the requirements of IGE/GM/6. |  |  |  |
| 6 | The meter installation is capable of sustaining a design maximum incidental pressure of 200 mbar at the inlet of the meter installation without jeopardizing the integrity of any connected gas fittings, and shall have an associated Design Pressure of 75mbar. |  |  |  |
| 7 | The meter installation will ensure that gas flow rates greater than 5% of the maximum allowable flow rates, the operating pressure at the outlet on the meter installation is maintained between 15 – 25 when the pressure at the inlet of the meter installation is between DMP 19 and MOP 75 mbar. |  |  |  |
| 8 | That the meter and installation meets the requirements of Schedule 2B of the Gas Act with respect to compliance with Section 17 of the Gas Act. |  |  |  |
| 9 | That the company responsible for undertaking the installation has the appropriate GAS SAFE registration and that the individual who undertakes the work holds an appropriate and valid certificate of competence under Nationally Accredited Certification Scheme or Approved Code of Practice. |  |  |  |
| 10 | In the event that my organisation is not OAMI registered, the installation will be inspected by an OAMI in accordance with the Gas Suppliers Standard Licence Conditions. |  |  |  |
| 11 | Signed _______________________________ Organisation installing meter installation |  |  |  |
| 12 | Date _________________________________ |  |  |  |
| 13 | Position in Organisation ___________________________________ |  |  |  |

* Where applicable

# Delete as appropriate

| 14 | Section B to be completed by the organisation requesting Authorisation to break a seal, set and seal the meter regulator. |
| --- | --- |
| 15 | The regulator will be set to ensure a metering pressure of [ ] mbar7 |
| 16 | The regulator lock up pressure will not exceed [ ] mbar7 |
| 17 | Under all circumstances (including zero flow) the meter installation will protect the installation pipe work, gas fittings and any appliances from being exposed to pressures greater than [ ]9 mbar. Any bypass arrangements, if fitted, will ensure this requirement is always met. |
| 18 | The meter installation will be clearly labelled with its metering pressure. |
| 19 | That the company responsible for undertaking any setting or adjustment has the appropriate GAS SAFE registration and that the individual who undertakes the work holds an appropriate and valid certificate of competence under nationally accredited certification scheme or approved code of practice. |
| 20 | I confirm that this organisation is an OAMI and request Authorisation to break a seal, set and seal the meter regulator. I also confirm that a GAS SAFE registered person with appropriate competencies for this category of work will verify and ensure that the meter regulator, when installed and put to work will not exceed the values stated above. In the event that the meter regulator is adjusted the meter regulator will be subsequently sealed to prevent unauthorised adjustment with a seal marked with this organisation’s OAMI registration number. |
| 21 | Signed ________________________ Organisation requesting to break a seal, set and seal the meter regulator. |
| 22 | Date ________________________ |
| 23 | Position in Organisation ______________________ e.g. Responsible Engineer/Manager |
| 24 | Section C For National Grid Gas Office use only |
| 25 | Date received: ________________ |
| 26 | Application reference number: ________________________ |

7 Reference should be made to Appendix B for appropriate values.

9 Reference should be made to Appendix B to insert the appropriate value for regulator lockup.

FORM C4A

| LINE NO | REQUEST FOR AUTHORISATION TO UNDERTAKE THE SETTING AND SEALING OF THE METER REGULATOR AND ANY ASSOCIATED PRESSURE CONTROL AND PROTECTIONS DEVICE(S) ON A LOW PRESSURE, NON STANDARD, OR HIGHER PRESSURE METER INSTALLATION WITH A METERING PRESSURE OF 21 MBAR. |  |  |  |
| --- | --- | --- | --- | --- |
| 1 | Name and address of organisation submitting this request and installing the meter installation. (Correspondence Address) |  | OAMI Number* (If applicable) |  |
|  |  |  | GMAM Registration Number* (Mandatory unless the supply point is subject to a Network exit agreement) |  |
| 2 | Name and address of OAMI requesting Authorisation to break a seal, set and seal the meter regulator and any associated pressure control and protection device(s). |  | OAMI Number (Mandatory) |  |
| 3 | Address where meter installation is to be installed. |  |  |  |
| 4 | MPRN or Confirmed Quotation Reference. |  |  |  |
| 5 | Section A to be completed by the organisation requesting to install the meter installation |  |  |  |
| 6 | I/We# warrant that this meter installation of the category defined above and installed or modified by this organisation following receipt of National Grid Gas’s Letter of Authorisation will meet the following conditions: |  |  |  |
| 7 | The meter installation is designed and will be installed to comply with the requirements of the following standards. [IGE/GM/1, IGE/GM/4, IGE/GM/8]1 |  |  |  |
| 8 | The meter installation will be regulated and the pressure control and protection arrangements of the installation will comply with [ ]2 |  |  |  |
| 9 | The meter installation is capable of sustaining a design maximum incidental pressure at the inlet of the meter installation of [ ] 4 without jeopardising the integrity of any connected gas fittings, and shall have an associated Design Pressure of [ ] 4. |  |  |  |
| 10 | The meter installation will ensure that at flow rates greater than 5% of the maximum allowable flow rate, the operating pressure at the outlet on the meter installation is maintained between 15 – 25 mbar when the pressure at the inlet of the meter installation is between DMP [ ] and MOP [ ]6. |  |  |  |

	Where applicable

	Delete as appropriate

1	The applicant should state those standards to which the meter installation will designed.

2	The applicant should state what pressure control and protection standard that is to be used and where a number of options are available to state which option is to be used.

4	The applicant should determine the design maximum incidental pressure from table 3, which corresponds to the pressure tier of the Network for which the meter installation is to be connected.

6	The Design Minimum Pressure and the Maximum Operating Pressure as provided by National Grid Gas for the Network should be inserted at this point.

| 11 | That the meter and the installation meet the requirements Schedule 2B of the Gas Act with respect to compliance with Section 17 of the Gas Act. |
| --- | --- |
| 12 | That the person undertaking the installation is GAS SAFE registered and has been assessed by our organisation as competent for this category of work, |
| 13 | In the event that my organisation is not OAMI Registered, the installation will be inspected by an OAMI in accordance with the Gas Suppliers Standard Licence Conditions. |
| 14 | Signed ________________________Organisation installing meter installation |
| 15 | Date ________________________ |
| 16 | Position in Organisation _________________ |
| 17 | Section B to be completed by the organisation requesting Authorisation to break a seal, set and seal the meter regulator and any associated pressure control and protection device(s). |
| 18 | The regulator will be set to ensure a metering pressure of [ ] mbar7 |
| 19 | The regulator lock up pressure will not exceed [ ] mbar7 |
| 20 | The relief valve will be set to open at a pressure of [ ] mbar7 |
| 21 | The final safety device will be set at a pressure of [ ] mbar7 |
| 22 | Under all circumstances (including zero flow) the meter installation will protect the installation pipe work, gas fittings and any appliances from being exposed to pressures greater than [ ] 8 mbar. Any bypass arrangements, if fitted, will ensure this requirement is always met. |
| 23 | The meter installation will be clearly labelled with its metering pressure, the pressure any relief valve will open and the limiting pressure of any final protection device. |
| 24 | That the person undertaking any setting or adjusting is GAS SAFE registered and has been assessed by our organisation as competent for this category of work. |
| 25 | I confirm that this organisation is an OAMI and request Authorisation to break a seal, set and seal the meter regulator and any associated pressure control and protection device(s). I also confirm that a GAS SAFE registered person with appropriate competencies for this category of work will verify and ensure that the regulator and any associated pressure control and protection device(s), when installed and put to work will not exceed the values stated above. In the event that the meter regulator and any associated pressure control and protection device(s) are adjusted the meter regulator and any associated pressure control and protection device(s) will be subsequently sealed to prevent unauthorised adjustment with a seal marked with this organisation’s OAMI registration number. |
| 26 | Signed ________________________ Organisation requesting to break a seal, set and seal the meter regulator and any associated pressure control and protection device(s). |
| 27 | Date ________________________ |
| 28 | Position in Organisation _________________ e.g. Responsible Engineer/Manager |

7   Reference should be made to Appendix B for appropriate values

8   Insert the appropriate pressure of the final protection device, normally the set pressure plus the tolerance.

| 29 | Section C For National Grid Gas Office use only |
| --- | --- |
| 30 | Date received: ________________ |
| 31 | Application reference number: ________________________ |

FORM C4B

| LINE NO | REQUEST FOR AUTHORISATION TO UNDERTAKE THE SETTING AND SEALING OF THE METER REGULATOR AND ANY ASSOCIATED PRESSURE CONTROL AND PROTECTIONS DEVICE(S) ON A LOW PRESSURE, NON STANDARD OR HIGHER PRESSURE METER INSTALLATION WITH A METERING PRESSURE OTHER THAN 21 MBAR. |  |  |  |
| --- | --- | --- | --- | --- |
| 1 | Name and address of organisation submitting this request and installing the meter installation (Correspondence Address) |  | OAMI Number* (If applicable) |  |
|  |  |  | GMAM Registration Number* (Mandatory unless the supply point is subject to a Network exit agreement) |  |
| 2 | Name and address of OAMI requesting Authorisation to break a seal, set and seal the meter regulator and any associated pressure control and protection device(s). |  | OAMI Number (Mandatory) |  |
| 3 | Address where meter installation is to be installed |  |  |  |
| 4 | MPRN or Confirmed Quotation Reference |  |  |  |
| 5 | Section A to be completed by the organisation requesting to install the meter installation |  |  |  |
| 6 | I/We# warrant that this meter installation of the category defined above and installed or modified by this organisation following receipt of National Grid Gas’s Letter of Authorisation will meet the following conditions: |  |  |  |
| 7 | The meter installation is designed and will be installed to comply with the requirements of the following standard [ ]1 |  |  |  |
| 8 | The meter installation will be regulated and the pressure control and protection arrangements will comply with [ ]2 or The meter installation will be unregulated and this organisation has obtained an exemption certificate under Regulation 40 of the Gas Safety (Installation and Use) Regulations 19983 |  |  |  |
| 9 | The meter installation is capable of sustaining a design maximum incidental pressure at the inlet of the meter installation of [ ] 4 mbar without jeopardising the integrity of any connected gas fittings. and shall have an associated Design Pressure of [ ] 4. |  |  |  |

	Where applicable

	Delete as appropriate

1	The applicant should state those standards to which the meter installation will be designed.

2	The applicant should state what pressure control and protection standard that is to be used and where a number of options are available to state which option is to be used.

3	If the meter installation is regulated then this paragraph shall be struck through. If the meter installation is unregulated then a copy of the Exemption certificate arising from GS(IU)R Reg.40 shall be attached

4	The applicant should determine the design maximum incidental pressure from Table 3, which corresponds to the pressure tier of the Network for which the meter installation is to be connected.

| 10 | The meter installation will ensure that at flow rates greater than 5% of the maximum allowable flow rate, the operating pressure at the outlet of the meter installation is maintained between [ ] and [ ]5 when the pressure at the inlet of the meter installation is between DMP [ ] and MOP [ ]6 |
| --- | --- |
| 11 | That the meter and the installation meet the requirements of Sec Schedule 2B of the Gas Act with respect to compliance with Section 17 of the Gas Act. |
| 12 | That the person undertaking the installation is GAS SAFE registered and has been assessed by our organisation as competent for this category of work. |
| 13 | In the event that my organisation is not OAMI Registered, the installation will be inspected by an OAMI in accordance with the Gas Suppliers Standard Licence Conditions. |
| 14 | Signed ________________________Organisation installing meter installation |
| 15 | Date ________________________ |
| 16 | Position in Organisation ___________________ |
| 17 | Section B to be completed by the organisation requesting Authorisation to break a seal, set and seal the meter regulator and any associated pressure control and protection device(s). |
| 18 | The regulator will be set to ensure a metering pressure of [ ] mbar7 |
| 19 | The regulator lock up pressure will not exceed [ ] mbar7 |
| 20 | The relief valve will be set to open at a pressure of [ ] mbar7 |
| 21 | The final safety device will be set at a pressure of [ ] mbar7 |
| 22 | Under all circumstances (including zero flow) the meter installation will protect the installation pipe work, gas fittings and any appliances from pressures greater than [ ] mbar8. Any bypass arrangements, if fitted, will ensure this requirement is always met. |
| 23 | The meter installation will be clearly labelled with its metering pressure, the pressure the relief valve will open and the limiting pressure of the final protection device. |
| 24 | That any person undertaking any setting or adjustment is GAS SAFE registered and has been assessed by our organisation as competent for this category of work. |
| 25 | I confirm that this organisation is an OAMI and request National Grid Gas Authorisation to break a seal, set and seal the meter regulator and any associated pressure control and protection device(s). I also confirm that a GAS SAFE registered person with appropriate competencies for this category of work will verify and ensure that the regulator and any associated pressure control and protection device(s), when installed and put to work will not exceed the values stated above. In the event that the meter regulator and any associated pressure control and protection device(s) are adjusted the meter regulator and any associated pressure control and protection device(s) will be subsequently sealed to prevent unauthorised adjustment with a seal marked with this OAMI registration number. |

5	Insert the minimum and maximum pressure conditions that are applicable for the installation pipework and gas appliance(s) that will be supplied through the meter installation, please attach supporting letter from consumer.

6	The Design Minimum Pressure and Maximum Operating Pressure as provided by National Grid Gas for the Network should be inserted at this point.

7 Reference should be made to Appendix B for appropriate values.

8 Insert the appropriate pressure of the final protection device, normally the set pressure plus the tolerance.

| 26 | Signed ________________________ Organisation requesting to break a seal, set and seal the meter regulator and any associated pressure control and protection device(s). |
| --- | --- |
| 27 | Date ________________________ |
| 28 | Position in Organisation _________________ e.g. Responsible Engineer/Manager |
| 29 | Section C For National Grid Gas Office use only |
| 30 | Date received: ________________ |
| 31 | Application reference number: ________________________ |