Faulty Equipment Queries

(Supplier Guidelines)

CONTENTS

Page

Introduction & Definitions								3

- What is a FEQ?

- What is NOT a FEQ?

- Contractual Definition & Obligations

- FEQ Performance Measurement

FEQ Submission Requirements	                                        7

- FEQ Query Submission Template

The Effective Management of FEQ Queries	       	      9

- Validation Checks

- Understanding what the fault might be – Hints & Tips

- Data Clarification Requests - ADI’s

- End User Delays – EUD’s

- Out of Hours Work Requests

- PSQ’s

- Root Cause

- Reducing Invalid Queries

Useful Reference Material			                          17

Glossary of Terms  							            18

Appendix A – Site Visit Attendance Contractual SLA’s                  23

# Introduction & Definitions

The purpose of this guidelines document is to provide Gas Suppliers with some reference material on the subject of managing queries relating to faulty I & C metering equipment (known as FEQ queries).

Under the terms of The Provision and Maintenance Contract, Gas Suppliers are entitled to a refund of rental charges for any metering equipment which is found to have been faulty. The refund is calculated based on the daily rental charge from the date on which the fault was notified until the date on which the fault is rectified. It is therefore important for Gas Suppliers to follow the correct procedure when raising a FEQ query.

Due to the varied nature of the I & C market, particularly with the increasing amount of Automatic Meter Reading (AMR) equipment being installed, there are many different scenarios where an End Consumer might believe that a fault has arisen.

This guide seeks to raise awareness of when and how a FEQ query should be raised with National Grid Metering and the steps to be taken before raising a  query.

What is a FEQ?

A FEQ query is defined as any query reporting a possible fault against an I & C sized meter or meter installation where the gas supply has not been interrupted.

For the avoidance of doubt FEQ queries can only be raised against meters with a badged capacity greater than 11 scmh (i.e. NOT domestic U6 sized meters)

FEQ queries can be raised in relation to faulty I & C sized  meters, regulators, converters, flow computers, electrical isolation barriers and ancillary equipment.

Please note: Automatic Meter Reading Equipment including telemetry and Dataloggers are not the responsibility of National Grid Metering and are therefore outside of the FEQ process.

It is also important to remember that AMR equipment may be disconnected during the investigation of a FEQ query. It is the responsibility of the Gas Supplier to arrange for AMR equipment to be reconnected regardless of the outcome of the query.

What is NOT a FEQ?

Domestic Sized Meter Faults

If End Consumers notify Gas Suppliers of a fault with a U6 (Domestic) sized meter, then regardless of market sector, it should be raised via the Portal, IX or manually as a faulty   meter exchange work request rather than a FEQ query.   (Transaction Type = EXCHG, Transaction Type Reason Code = FULTY).

Damaged or Vandalised Meters

Meters that have been damaged or vandalised but are still passing gas do not fall under the FEQ process.  Gas Suppliers should raise chargeable work requests for replacements to be supplied.

Domestic Sized Non-Pulsing Meters

It is currently not appropriate for Gas Suppliers to request meter exchanges for domestic meters simply because the meter is not pulse enabled. National Grid Metering’s position is that a non pulsing domestic sized meter is fit for purpose.

* Please note this is  currently under review and may change in the future

“Gas off” Faults

In situations where Gas Suppliers are notified of a fault with an I & C meter or metering installation and the gas supply has been interrupted, a TFM work request should be raised by calling the TFM Line (0870 0600005).

Requirement to Upgrade or Downgrade the Meter Installation

When dealing with potential faults, it is important to note that National Grid Metering’s responsibility is to maintain the existing meter to ensure that it is fit for the purpose for which it was originally designed.

Before submitting a FEQ query, Gas Suppliers should seek clarification regarding current site conditions. Gas use requirements can and often do change considerably over time. So if for example, a fault is reported by an End Consumer at a site where a rotary meter is installed and there have been no readings for some time, then prior to raising an FEQ query please check to see what appliances are being used/gas usage in comparison to the amounts originally specified. (Meter capacity information can be found on page 16).

If the gas use at the site has decreased, it is quite possible for insufficient gas to be passing through the rotary meter to make it turn.  In these circumstances, the rotary meter is not faulty. It is the changing site conditions that have resulted in the rotary meter being unable to record the smaller volume of gas now being used. A downgrade to a smaller meter may be the most appropriate course of action.  This would be a chargeable work request and not a FEQ query.

Conversely, If a site has expanded and additional or replacement appliances have been installed it is quite possible that the site could experience operating difficulty often in the form of low gas pressure. In these circumstances it is equally important for Gas Suppliers to clarify the current site gas use requirements. Making a note of the input rating which can be found on the badge of all new gas appliances is particularly important in these circumstances to enable Gas Suppliers to advise their Customers what type of meter installation may be required.

National Grid Metering will always be happy to provide guidance and support in circumstances where Gas Suppliers believe that a replacement meter installation may be required.

It is however, in the best interests of all parties to avoid submitting a FEQ query in these circumstances. Whilst investigating a FEQ query, National Grid Metering will check to make sure that the existing meter is working in accordance with its original specifications. If the site conditions have changed, processing a FEQ query that results in no fault being found serves little or no purpose. This could also result in an avoidable delay in terms of establishing the best solution for the Customer.   It is therefore, it is in all parties’ interests for Gas Suppliers to pro-actively seek clarification of their customers’ current gas use requirements before submitting a FEQ query.

Contractual Definition & Obligations

Sections 3.0 – 7.2 of The Provision and Maintenance of Metering Equipment Contract set out the contractual requirements between National Grid Metering and Gas Suppliers with regard to unplanned maintenance for all meter types, meter equipment, metering pressures and ancillary equipment.

Depending on the type of meter, metering equipment or the metering pressure, National Grid Metering has a contractual obligation to attend site within clearly defined timescales. (See Appendix A)

# FEQ Performance Measurement

FEQ queries can have one of two possible resolutions. The metering equipment will either be tested and found to be in need of repair or replacement (valid FEQ) or it will be tested and found to be working in accordance with its original specifications (invalid FEQ). National Grid Metering’s FEQ performance is calculated by looking at the time taken to resolve both valid and invalid FEQ queries.

National Grid Metering is contractually obliged to investigate and resolve 92% of FEQ meter related queries and 95% of converter faults within 20 working days.  (Contract Modification Request 43a was raised for enhanced performance levels with effect from April 2011.

FEQ Query Submission Requirements

When submitting a FEQ query, Gas Suppliers should provide the following information using the submission Template contained on Page 8.  The more information provided in the query, the more likely National Grid Metering will be in a position to diagnose the problem, respond and resolve in a timely manner:

- MPRN

- Meter / Converter Serial Number

- Supplier Query Contact Details (name,  email address & telephone number)

- Confirmation that the site is currently using gas and ideally, current site load requirements

- Explanation of the fault to include as a minimum:

  - A clear explanation of how the fault was notified. For example, was it the end user, an MRA or other third party (AMR provider)

  - If the query claims that the meter is not pulsing correctly Gas Suppliers should explain specifically what leads them to believe that the meter may be at fault

If the above information is not provided or if it appears unclear in any way, National Grid Metering’s FEQ Team should telephone the person who raised the query to ask for the missing information and discuss the background to the query.

If it is not possible to make contact by telephone, a data clarification request should be submitted by National Grid Metering. If telephone contact is made but it is not possible for an immediate response to be provided, National Grid Metering will follow up the call with a data clarification request. This will ensure that the query resolution performance standards are not adversely affected by delayed responses from Gas Suppliers to requests for additional information.

Finally, Gas Suppliers should be aware that if they are reporting a possible fault with a meter that has AMR equipment attached, the engineer may disconnect the AMR equipment during the process of checking the meter.  Gas Suppliers are responsible for arranging the re-connection of the AMR equipment.

So before submitting a FEQ query, it is important for the Gas Supplier to have spoken with their End Consumer and the AMR provider if applicable to make sure that there are no known faults with the AMR equipment.

FEQ Query Submission Template

FEQ Query Description Example

End Consumer* / MRA* / AMR Provider* (*delete as appropriate) has advised us that there is a fault with the meter / converter at the following address***************, MPRN*********. The meter / converter serial number is**********.

Before submitting this query, we have spoken to our Customer and advised them that

- If a replacement meter is required, the gas supply will be interrupted during the installation process.  The Customer understands this and will provide reasonable access to our engineers.

- If AMR equipment is installed, National Grid Metering’s engineers may disconnect the equipment during the process of examining the reported fault. The AMR will not be reconnected by National Grid Metering. An approved installer will need to be employed to make the re-connection.

We have checked and can confirm that there is* / there is not* (*delete as appropriate) AMR equipment installed.  If AMR equipment has been installed, we confirm that we have checked with the AMR provider and they have confirmed that there is no known fault with the AMR equipment. The AMR provider is *********** and their contact details are Name*********, Telephone Number***********, email address*****************.

We can also confirm that we have checked to make sure that the meter is not domestic sized i.e. U6, E6 or G4 and that the site is currently using gas.

Our supply contract states that the annual gas usage for the site is ******Kwh. The site has the following appliances*****************************. The input capacity for each appliance is************************************** .  The site contact details are Name***********, Telephone Number***********,email address************.

The specific fault details are: ***************************************************************************************************************************************************************************************************************************************************************************************************************************************************************************************.

Query raised by Name********************,Telephone Number*****************,

email address****************************.

The Effective Management of FEQ Queries

Validation Checks

On receipt of a FEQ query the following checks will be completed before National Grid Metering commence any investigation.  Gas Suppliers should take the time to ensure that the following criteria are met before submitting a FEQ Query.

- Is it a National Grid Asset?

Do the asset details contained within the query match the details held in Rainbow? If there is any doubt, National Grid Metering will contact the person who raised the query or raise an ADI and request clarification before taking any further action. Details of non National Grid Owned Meters can be found in the useful reference material section (page 16).

- Is there a live MPRN?

In circumstances where there is no live MPRN in Rainbow, meter ownership should first be established.  If found to be a National Grid –owned meter then Gas Suppliers should  raise either a Found Meter Query or a Rainbow appointment file flow with transaction type code “FNDAS”.

Gas Suppliers are able to nominate what is known as an “effective date“ for the “FNDAS” appointment file flow for the day after the flow is submitted. So there is no reason for Suppliers to ask us to investigate a fault with a found meter before the meter is set up in Rainbow.

- Is the meter capacity greater than 11SCMH?

Please check the meter size. If the meter is domestic sized, an FEQ query should not be submitted.  If Gas Suppliers are notified of a fault with a  U6 sized  meter, then regardless of market sector it should  be raised as a faulty meter exchange work request via the Portal , IX or as a Manual Work Request.   (Transaction Type = EXCHG, Transaction Type Reason Code = FULTY for the ORJOB or FAULTY for the Web Portal based job).

- Is AMR Equipment Installed?

Please check to find out whether AMR equipment is installed before submitting a FEQ Query.  If there is any doubt, please ask the End Consumer to confirm.

On some occasions, it is possible that National Grid Metering has been notified that AMR equipment has been installed but the Gas Supplier has not been informed.  If National Grid Metering identifies that AMR equipment has been installed but the Supplier has not confirmed this in the query explanation, National Grid Metering should telephone the query instigator to ask for more information regarding the fault (see hints & tips section for details on the type of questions that may be asked).

If the Gas Supplier is unable to provide an immediate response over the telephone, a data clarification request will be raised. This will ensure that National Grid Metering’s contractual query resolution performance standards are not adversely affected by a delayed response.

Understanding what the fault might be – Hints & Tips

Once the validation checks have been completed, National Grid Metering can begin the process of diagnosing the fault.  There are many different scenarios so it is crucial for Gas Suppliers to provide as much detail as possible in the query description to enable National Grid Metering to understand what might be wrong and to provide the most appropriate solution.

So before submitting an FEQ Query please take time to collate the following information:

- What specifically is wrong with the equipment?

- When did the problem first arise?

- How was the Supplier notified of the fault?

- What are the current site gas use requirements?

If the fault was notified by a third party (MRA / AMR installer), National Grid Metering should call the query instigator and request details of exactly what was reported. A data clarification request will be raised if this information is not supplied and it has not been possible to clarify the details immediately over the telephone.

- Have any other FEQ’s been raised within the past 6 months?

Please check to see if you have raised any previous queries. This might be significant in terms of the query diagnosis.  Was the Gas Supplier required to take further action or supply further information? Has this been done?

If not, National Grid Metering may reject the query with reference being made to the earlier query response.  If there is any doubt after having reviewed previous responses National Grid Metering should investigate further.

- When AMR equipment is attached

If there is AMR equipment attached, Gas Suppliers and National Grid Metering should check the date it was installed and compare the AMR installation date to the date the reported fault developed.  Before submitting a FEQ query, it would be helpful if Gas Suppliers could find out whether the reported fault might be due to read information being misinterpreted in the period since the AMR equipment was installed.

National Grid Metering should also ask the query instigator to confirm whether any problems have been reported either to or by the AMR installer. If so, Suppliers should be prepared to share the information if required in order to establish whether or not the metering equipment is faulty. National Grid Metering may request specific information from the AMR provider (such as a copy of their fault report).

- Meter Pulse Faults

For Meter Pulse Reported Faults, please check whether the meter is pulse capable using the information supplied by National Grid Metering each month.  If the meter is not pulse capable, Gas Suppliers should not raise a FEQ query. A Guaranteed Pulse Work Request should be raised in order for the meter to be exchanged with a pulse capable replacement.

For LF Switch related queries, on pulse capable meters or for queries where meters are reported as either under or over pulsing, Gas Suppliers should be ready to provide the following details to help with the fault diagnosis:

- Who determined that there was a fault?

- How was the determination made?

- What does the engineer’s report say?

Data Clarification Requests (ADI’s)

There are many different types of I & C meters and converters and because of the diverse nature of the I & C market, there are many different scenarios that could lead a  Gas Supplier to suspect that there may be a fault with one of National Grid Metering’s assets.

Data clarification requests (ADI’s) provide a means for National Grid Metering to ask Suppliers to provide more specific information to help resolve a FEQ query.

‘Data Clarification’ is a Rainbow query status that indicates that National Grid Metering has requested additional information from a Gas Supplier, and that the progress of the query is pending the Supplier’s response. As soon as a data clarification request has been raised, the clock measuring our response time is stopped.  From an SOS viewpoint, the clock does not begin ticking again until a response is received from the Gas Supplier.

A response is always required to an ADI request.  Continuous dialogue between National Grid Metering and Gas Suppliers regarding the provision of clearly worded and correctly submitted FEQ queries should help to minimise the number of data clarification requests issued and also reduce the volume of invalid queries.

Gas Suppliers have a 20 working day period in which to respond to an ADI request. A “chaser” will be sent after 10 working days but if the Supplier fails to respond within the 20 working day window, the query is automatically closed down and classified as invalid.

End User Delays

There will be scenarios where, for example, end users will delay the installation of a replacement meter because they don’t want to disrupt their business activities.  In such cases, an End User Delay status can be assigned to an FEQ query in the same way as an ADI request. End User Delays also serve to stop the SOS clock. National Grid Metering will seek approval with Gas Suppliers for a query to be closed if the end user delay reaches 30 working days.

Out of Hours Work Requests

Gas Suppliers and their Customers may occasionally request out of hours appointments for replacement metering equipment to be installed.

National Grid Metering has no contractual obligation to work outside of normal business hours and our Service Providers charge additional sums for any work completed during evenings and weekends. National Grid Metering therefore reserves the right to pass any out of hours work related costs on to the Gas Supplier.

Agreement must be reached between Gas Suppliers and National Grid Metering regarding any additional costs before any OOH work request is raised.

RE-SUBMITTED QUERIES (PSQ) & Repeat Queries

Gas Suppliers may choose to challenge the validity of the resolution of a FEQ query (typically where no fault was found after completing the initial investigation).

Gas Suppliers have 12 business days following the original resolution date in which to raise a PSQ. It is important that the PSQ specifically challenges the original response and also explains why with as much information to substantiate the challenge as possible.

If Gas Suppliers choose not to submit a PSQ, they do have the option of submitting a further FEQ query at a later stage.

Root Cause

When National Grid Metering close an FEQ query, a suitable root cause code will be applied to identify what caused the query to be raised. Root cause reporting and analysis provides all parties with valuable information in terms of potential actions to minimise invalid queries from being raised and to identify trends or patterns regarding the type of faults being reported.

REDUCING INVALID QUERIES

When a query is resolved by National Grid Metering it must be categorised as either Valid or Invalid.

By working closely with National Grid Metering, sharing information and feeding back examples we have the opportunity to improve our working relationships, improve understanding both ways and also reduce the number of invalid queries.

There is a joint benefit for Gas Suppliers and National Grid Metering to reduce the amount of invalid queries submitted.  Listed below are examples of some of the most common reasons why a FEQ query might be classed as invalid.

No Response to a Data Clarification Request (ADI)

Gas Suppliers have 20 business days to respond to an ADI. If no substantial response is received within these 20 days National Grid Metering will close the query.

No Response to an End User Delay (EUD)

Gas Suppliers / End Users have 30 business days to respond to an EUD. If no substantial response is received within 30 business days National Grid Metering will seek agreement for the query to be closed.

Where submission reason is incorrect

For example the Supplier claims that their Customer’s meter is not working correctly   but it is established that they were not using any gas.

Third Party Meters

If the meter in question is a non National Grid meter, the query will be closed and classified as invalid.  Before submitting FEQ queries Gas Suppliers should check with the End Consumer or if in doubt, the previous Supplier to confirm whether the meter is third party owned.

:

# Useful Reference Material

Meter Capacity Table

Identifying Non National Grid Metering Owned Meters

Converter guide

Publications & Useful External Phone Numbers

On National Grid Meterings Web Site you can find the following useful documents under the “publications” section;

Metering Charges - latest metering prices

http://www.nationalgrid.com/uk/Metering/Publications/Metering+Charges/

MAM Manual – providing details on file formats

http://www.nationalgrid.com/uk/Metering/Publications/mam_manual/

IS Helpline:   08705 216 121 (for technical problems when using the Web Portal)

Xoserve:   0845 601 3048

# Glossary of Terms

“AMR Device”: shall mean an electronic device connected to a Meter or Converter which reads the number of pulses generated from the Meter or Converter and which interprets, stores and transmits data to a collection system at predetermined intervals via an appropriate communication medium;

“Ancillary Equipment”: shall mean:

(a)	 where it is attached to, or is to be attached to, a Meter with a badged 	capacity of less than 11 SCMH:

(i) 	a Meter Regulator;

(ii)	 the flexible or rigid pipe (and any metal fittings and/or washers comprised in

or attached to such pipe) connecting the Emergency Control Valve on the

National Grid System to the Meter Regulator;

(iii) 	the BS 746 fitting (and any metal fittings and/or washers attached to such

fitting) connecting the Meter Regulator to the Meter;

(iv) 	the Meter shelf or bracket (where fitted) unless such bracket comprises part

of a Meter Housing; and

(v) 	the flexible pipe connecting a semi concealed meter installed in a semi

concealed Meter Housing to the brass outlet fitting in the Meter Housing

including any washers attached to it (where applicable);

(b) 	where it is attached to, or is to be attached to, a Meter with a badged              capacity of 11	SCMH or above:

- any Meter Regulator;

(ii) 	associated pre heaters connected to the Meter together with any associated

valves, filters, flexible connectors, seals, meter by pass, interconnecting

pipework, cables, fittings brackets and supports; and

(iii) 	any Meter Housing owned by National Grid, but it shall not include in the case of either (a) or (b) any associated fittings, pipework, nstallation(s) or Meter Housing owned by the Customer or a Consumer, or	any third party;

“Converter”: shall have the same meaning as "conversion device" (as such term is defined in the Institution of Gas Engineers and Managers publication: IGE/GM/5 Edition 2) being an instrument for calculating the volume of gas at a pre-defined standard temperature and pressure which is equivalent to the volume of gas at actual temperature and pressures recorded as passing through a Meter;

“Crime Number”: shall mean the number assigned in respect of a police report which states that theft or damage of a Meter occurred and the time and date of such theft or damage as reported to the police;

“Daily Read Equipment”: shall mean equipment of a design and manufacture specified by National Grid which enables Meter Readings to be obtained by National Grid (Gas

Transporter) remotely at set intervals, such equipment comprising:

(a) a device for capturing from the Meter, and/or (where installed) a Converter, data which constitutes or permits the derivation of a Meter Reading; and

(b) a telephone line or radio transmitter and/or such other equipment as shall be required for transmitting such data to National Grid (Gas Transporter);

“Electrical Isolation Barrier”: shall mean a device providing multiple volt free signals

incorporating electrical isolating barriers to limit the amount of energy that may pass between any electrical equipment connected to the Metering Equipment;

“Flow Computer”: shall mean a device for use with an Orifice Plate Meter that fulfils the same functions as a Converter;

“High Pressure”: shall mean gas pressure exceeding 7 bar at the outlet of the Emergency Control Valve and a Meter or Ancillary Equipment which is described as a High Pressure Meter or High Pressure Ancillary Equipment shall mean that it is designed to operate at High Pressure;

“Installation Pipework”: shall mean all pipe and gas consuming facilities installed or to be installed downstream of the Metering Equipment;

“Intermediate Pressure”: shall mean gas pressure exceeding 2 bar but not exceeding 7 bar at the outlet of the Emergency Control Valve and a Meter or Ancillary Equipment which is described as an Intermediate Pressure Meter or Intermediate Pressure Ancillary Equipment shall mean that it is designed to operate at Intermediate Pressure;

“Low Pressure”: shall mean gas pressure not exceeding 75mbar at the outlet of the

Emergency Control Valve and a Meter or Ancillary Equipment which is described as a Low Pressure Meter or Low Pressure Ancillary Equipment shall mean that it is designed to operate at Low Pressure;

“Medium Pressure”: shall mean gas with a maximum operating pressure exceeding 75mbar but not exceeding 2 bar at the outlet of the Emergency Control Valve and a Meter or Ancillary Equipment which is described as a Medium Pressure Meter or Medium Pressure Ancillary Equipment shall mean that it is designed to operate at Medium Pressure;

“Meter”: shall mean a measuring instrument that measures the volume of natural gas passing through it, with a specific badged capacity that is in accordance with Schedule 2B of the Gas Act;

“Meter By-pass”: shall mean any pipe, and associated gas fittings used in connection with it, used to supply gas to a Consumer without passing through the Meter, and thereby secure the continued offtake of gas at the Meter Point, in the event of any failure of, or any work on, part of the Metering Equipment which would impede the flow of gas through the Meter;

“Meter Reading”: shall mean:

(a) 	the reading of the index of the Meter; and

(b) 	where a Convertor is installed, the corrected and uncorrected readings of the

Converter;

except that where Daily Read Equipment and a Converter are installed a Meter 	Reading need	not include both the reading under paragraph (a) and the uncorrected reading under paragraph (b);

“Meter Regulator”: shall mean a device located in close proximity to a Meter which is used for the sole purpose of controlling the pressure of gas within the Meter and/or the Installation Pipework and which is not separated from the Meter by buried pipework, except for short lengths of pipework specifically included in the installation design for access purposes;

“Metering Equipment”: shall mean the Meter, and Ancillary Equipment and/or where

appropriate,  Converter, installed or to be installed at a Consumer’s Premises;

“Non National Grid Meter”: shall mean any Meter which is not provided by National Grid in accordance with this Agreement;

Orifice Plate Meter”: shall mean a Meter that inferentially measures gas flow by measuring the differential gas pressure each side of an in-line annular plate contained within the Metering Equipment and which includes an Electrical Isolation Barrier and a Flow Computer;

“Planned Maintenance”: shall mean a maintenance activity either instigated by National Grid or in response to a request from the Customer or Consumer where the maintenance activity does not require urgent attention;

"PRS3": shall mean the National Grid product specification for Meter Regulators for gas flow rates not exceeding 6 SCMH and inlet pressures less than 75mbar;

"PRS33": shall mean the National Grid product specification for Low Pressure Meter

Regulators of nominal diameter greater than or equal to 11/4 inch and for inlet pressures up to 75 mbar;

Prime Meter”: shall mean a Meter installed upstream of any other Meter comprised within a Sub-deduct Arrangement

“Purging”: shall mean the displacement of natural gas by air or inert gas, or the displacement of air or inert gas by natural gas;

“Rental Charge”: shall mean the appropriate charges as set out in the National Grid Metering Charges for the provision and maintenance of a Meter (and/or where applicable Ancillary Equipment and /or Converter) which is provided in accordance with this Agreement and (where appropriate) annualised installation charges;

“Rotary Meter”: shall mean a Meter that mechanically measures gas flow by the positive displacement of a discrete volume of gas displaced between two impellers;

“SCMH”: shall mean the flow rate of a standard cubic metre of gas per hour, a standard cubic metre of gas being that amount of gas which at a temperature of 15C and an absolute pressure of 1.01325 bar and being free of water vapour occupies one cubic metre;

“Sub-deduct Arrangement”: shall mean an arrangement of pipes and meters (for the

avoidance of doubt comprising a Prime Meter and at least one Sub-deduct Meter), installed before 1st March 1996, which National Grid has recognised as being such an arrangement, by which a part of the gas which is conveyed by the National Grid System to a Consumer Premises for the purposes of supply to those Consumer Premises, is further conveyed to other Consumer Premises for the purposes of supply to those other Consumer Premises;

“Sub-deduct Meter”: shall mean a Meter, other than a Prime Meter, that is comprised within a Sub-deduct Arrangement;

“Turbine Meter”: shall mean a Meter that inferentially measures gas flow by measuring the speed of turbine blades rotating in the gas stream;

Unplanned Maintenance”: shall mean a maintenance activity which is not Planned

Maintenance and is usually instigated by the Customer or Consumer in response to a

suspected fault or failure of the Metering Equipment;

“Ultrasonic Meter”: shall mean a Meter that inferentially measures gas flow by using time of flight of ultrasound pulses through the gas stream;

“Working Day”: shall mean a Day other than a Saturday, a Sunday, Christmas Day, Good Friday, or a Day which is a bank holiday within the meaning of the Banking and Financial Dealings Act 1971;

“Working Hours”: shall mean (i) for the purposes of Schedule Two, Part A, the hours between 8 a.m. and 8 p.m. on each Working Day, and between 9 a.m. and 5 p.m. on any other Day; and (ii) for any purposes other than Schedule Two, Part A, the hours between 8 a.m. and 8 p.m. on each Working Day;

Appendix A

Contractual SLA’s for attendance to site to rectify reported faults

SCHEDULE FOUR - MAINTENANCE OF NATIONAL GRID METERING EQUIPMENT

Section 3.2 Unplanned Maintenance T3.2A (Diaphragm Meters with a capacity not exceeding 160SCMH)

| Credit Meters – Unplanned Maintenance | Fault/Failure or Programmed Visit | Standard to Attend Site following request |
| --- | --- | --- |
| Credit Meter - Gas ON | Battery flag, Blank screen, Noisy Meter | D+5 Working Days |
| Credit Meter - Gas ON | Meter not registering | D+5 Working Days |
| Credit meter – Gas OFF | Meter jammed, not registering | T+4hours |
| Meter Pulse Utilisation – Gas ON | Meter pulse faulty or failed | D+5 Working Days |

Section 4.2 Unplanned Maintenance T4.2A (Rotary and Turbine meters)

| Rotary/Turbine Meter | Fault/Failure | Standard to Attend Site following request |
| --- | --- | --- |
| Rotary/Turbine Meter Fault – Gas On | Meter not registering, faulty index etc. | D+4 Working Days |
| Rotary/Turbine Meter – Gas Off | Meter jammed | T+4 hours |
| Meter Pulse Output Port (where available) | Meter pulse failed | D+4 Working Days |

Section 4.4 Unplanned Maintenance T4.4A (High Pressure Meters)

| Orifice Plate or Ultrasonic Meter | Fault/Failure | Standard to Attend Site following request |
| --- | --- | --- |
| Rotary/Turbine Meter Fault – Gas On | Meter not registering, faulty index etc. | T+6 Hours |
| Rotary/Turbine Meter – Gas Off | Meter jammed | T+6 Hours |
| Meter Pulse Output Port (where available) | Meter pulse failed | T+6 Hours |

Section 5.0 Unplanned Maintenance T5.2B (Convertors, Flow Computers and Electrical Isolation equipment)

| Unplanned Maintenance | Fault/Failure | Standard to Attend Site following request |
| --- | --- | --- |
| Flow Computer | Measurement error, system failure or power failure | T+6 Hours |
| Convertor | Measurement/conversion error, system failure or battery failure | T+6 Hours |
| Electrical Isolation Barrier where part of an Orifice Plate Meter | Pulse failure or battery failure | T+6 Hours |

Section 6.0 Unplanned Maintenance T6.1B (Ancillary Equipment – Low Pressure)

| Ancillary Equipment - Unplanned Maintenance | Fault/Failure | Standard to Attend Site following request |
| --- | --- | --- |
| Low Pressure Ancillary Equipment – Repair or Maintain | Ancillary Equipment failure | T+6 Hours |

Section 6.0 Unplanned Maintenance T6.2B (Ancillary Equipment – Medium Pressure)

| Unplanned Maintenance | Fault/Failure | Standard to Attend Site following request |
| --- | --- | --- |
| Medium Pressure Ancillary Equipment and Intermediate Pressure Ancillary Equipment | Ancillary Equipment failure repair or replace | T+4 Hours |

Section 7.0 Unplanned Maintenance T7.2A (Ancillary Equipment – High Pressure)

| Unplanned Maintenance | Fault/Failure | Standard to Attend Site following request |
| --- | --- | --- |
| High Pressure Ancillary Equipment – Gas ON | Ancillary Equipment failure repair or replace | T+6 Hours |
| High Pressure Ancillary Equipment – Gas OFF | Ancillary Equipment failure repair or replace | T+6 Hours |